EJ

| ELECTRICAL PANEL , A, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CCT. No. | CIRCUIT USE |  | BREAKER |  | VOLTS |  |  |  | WIRE AND CONDUIT SIZE |  | CCT. No. | CIRCUIT USE | BREAKER |  | VOLTS |  |  |  | WIRE AND CONDUIT SIZE |
|  |  |  | SIZE | POLES |  | " |  |  |  |  |  |  | SIZE | POLES |  | " |  | C, |  |
|  | WASHER/DRYER RECEPTACLE - ROOM 130 |  | 30A | 2 | 208 | 2500 |  |  | 3c#10 AWG |  | 2 | RANGE RECEPTACLE - ROOM 101S | 40A | 2 | 208 | 4000 |  |  | 3c#8 AWG |
| 3 |  |  |  |  |  |  | 2500 |  |  |  | 4 |  |  |  |  |  | 4000 |  |  |
| 5 | WASHER/DRYER RECEPTACLE - ROOM 1035 |  | 30A | 2 | 208 |  |  | 2500 | 3c#10 AWG |  | 6 | RANGEHOOD - ROOM 101S |  |  | 120 |  |  | 250 | 2c#12 AWG |
| 7 |  |  |  |  |  | 2500 |  |  |  |  | 8 | DISHWASHER - ROOM 1015 |  |  | 120 | 500 |  |  | 2c#12 AWG |
| 9 | PANEL 'B' & PANEL 'C' |  | 125A | 3 | 208 |  |  |  | AS NOTED |  | 10 | @) CONDENSING UNIT CU-1 | 30A | 2 | 208 |  | 1800 |  | AS NOTED |
| 11 |  |  |  |  |  |  |  |  |  |  | 12 |  |  |  |  |  |  | 1800 |  |
| " |  |  |  |  |  |  |  |  |  |  | 14 | (cu-2) CONDENSING UNIT CU-2 | 30A | 2 | 208 | 1800 |  |  | AS NOTED |
| 15 |  |  |  |  |  |  |  |  |  |  | 16 |  |  |  |  |  | 1800 |  |  |
| 17 | GENERATOR SET PANEL |  | 30A | 3 | 208 |  |  |  | AS NOTED |  | 18 | (CU-3) CONDENSING UNIT CU-3 | 30A | 2 | 208 |  |  | 1800 | AS NOTED |
| 19 |  |  |  |  |  |  |  |  |  |  | 20 |  |  |  |  | 1800 |  |  |  |
| 21 |  |  |  |  |  |  |  |  |  |  | 22 | (Ef-12) DRYER EXHAUST FAN EF-12 | 15A |  | 120 |  |  | 1440 | AS NOTED |
| 23 |  |  |  |  |  |  |  |  |  |  | 24 |  |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  |  |  | 26 |  |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  |  |  | 28 |  |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  |  |  | 30 |  |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  |  |  | 32 |  |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  |  |  | 34 |  |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  |  |  | 36 |  |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |  |  |  | 38 |  |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |  |  |  | 40 |  |  |  |  |  |  |  |  |
| 41 |  |  |  |  |  |  |  |  |  |  | 42 |  |  |  |  |  |  |  |  |
| VOLTAGE: 120/208VAC MAIN BREAKER: 200A MOUNTING: SURFACE |  | MAINS: 200A BREAKER I.C.: 10KA |  |  | PHASE: 3 WIRE: 4 FEEDER />S INDICATED |  |  |  | FED FROM: AS INDICATED LOCATION: AS SHOWN |  |  |  |  |  |  |  |  |  |  |

| MECHANICAL EQUIPMENT SCHEDULE |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | DESCRIPTION | ROOM# | VOLTAGE & PHASE |  | BRANCH WIRING |  | BREAKER SIZE | CIRCUIT NUMBER | TOTAL VA |  | REMARKS |
|  | AIR HANDLING UNIT AHU-1 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-23 | 840 | VA | DISCONNECT REQUIRED |
|  | AIR HANDLING UNIT AHU-2 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-25 | 840 | VA | DISCONNECT REQUIRED |
|  | AIR HANDLING UNIT AHU-3 | 115S | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-27 | 840 | VA | DISCONNECT REQUIRED |
|  | BOILER B-1 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-18 | 1440 | VA | DISCONNECT REQUIRED |
|  | BOILER 8-2 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-20 | 1440 | VA | OISCONNECT REQUIREO |
|  | BOILER 8-3 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-22 | 1440 | VA | DISCONNECT REQUIRED |
|  | BOILER 8-4 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-24 | 1440 | VA | DISCONNECT REQUIRED |
|  | FUEL PUMP FP-1 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-26 | 150VA EACH |  | DISCONNECTS REQUIRED |
|  | FUEL PUMP FP-2 | 118 |  |  |  |  |  |  |  |  |  |
|  | FUEL PUMP FP-3 | 118 |  |  |  |  |  |  |  |  |  |
|  | FUEL PUMP FP-4 | 118 |  |  |  |  |  |  |  |  |  |
|  | HEAT RECOVERY VENTILATOR HRV-1 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-28 | 460 | VA | DISCONNECT REQUIRED |
|  | HEAT RECOVERY VENTILATOR HRV-2 | 115S | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-34 | 250 | VA | RECEPTACLE REQUIRED |
|  | EXHAUST FAN EF-1 | 117 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-30 | 700 | VA | DISCONNECT REQUIRED |
|  | EXHAUST FAN EF-2 | 114 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-4 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-3 | 113 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-22 | 160 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-4 | 101 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-22 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-5 | 133 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-22 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-6 | 106S | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-12 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-7 | 108S | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-12 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-8 | 108 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-36 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | EXHAUST FAN EF-9 | 110 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-40 | 135 | VA | CONNECT TO TIMER SWITCH |
|  | RADON EXHAUST FAN EF-10 | 110 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-40 | 200 | VA | CONNECT TO TOGGLE SWITCH |
|  | EXHAUST FAN EF-11 | 111 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-41 | 200 | VA | TIE INTO REVERSE ACTING THERMOSTAT BY MECH |
|  | DRYER EXHAUST FAN EF-12 | 103S | 120V, | 10 | 2c#12 | AWG | 1P-15A | A-22 | 200 | VA | INTERLOCK TO RUN WHEN DRYER IS OPERATIONAL |
|  | CONDENSING UNIT CU-1 | OUTSIDE | 208V, | 10 | 2c#10 | AWG | 2P-30A | A-10/12 | 3600 | VA | DISCONNECT REQUIRED |
|  | CONDENSING UNIT CU-2 | OUTSIDE | 208V, | 10 | 2c#10 | AWG | 2P-30A | A-14/16 | 3600 | VA | DISCONNECT REQUIRED |
|  | CONDENSING UNIT CU-3 | OUTSIDE | 208V, | 10 | 2c#10 | AWG | 2P-30A | A-18/20 | 3600 | VA | DISCONNECT REQUIRED |
|  | PUMP P-1 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-24 | 250 | VA | DISCONNECT REQUIRED |
|  | PUMP P-2 | 118 |  |  |  |  |  |  | 250 | VA | DISCONNECT REQUIREO |
|  | PUMP P-3 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-26 | 250 | VA | DISCONNECT REQUIRED |
|  | PUMP P-4 | 118 |  |  |  |  |  |  | 250 | VA | DISCONNECT REQUIRED |
|  | PUMP P-5 | 118 | 208V, | 10 | 2c#12 | AWG | 2P-15A | B-29/31 | 850 | VA | DISCONNECT REQUIREO |
|  | PUMP P-6 | 118 |  |  |  |  |  |  | 850 | VA | DISCONNECT REQUIRED |
|  | PUMP P-7 | 118 | 208V, | 10 | 2c#12 | AWG | 2P-15A | B-33/35 | 850 | VA | DISCONNECT REQUIREO |
|  | PUMP P-14 | 118 |  |  |  |  |  |  | 850 | VA | DISCONNECT REQUIRED |
|  | PUMP P-8 | 118 | 120V, | 10 | 2c#12 | AWG | 1P-15A | C-28 | 500 | VA | DISCONNECT REQUIRED |
|  | PUMP P-9 | 118 |  |  |  |  |  |  | 500 | VA | DISCONNECT REQUIRED |
|  | PUMP P-10 | 118 | 208V, | 10 | 2c#12 | AWG | 2P-15A | C-30/32 | 450 | VA | DISCONNECT REQUIRED |
|  | PUMP P-11 | 118 |  |  |  |  |  |  | 450 | VA | OISCONNECT REQUIREO |
|  | PUMP P-12 | 118 |  |  |  |  |  |  | 450 | VA | DISCONNECT REQUIRED |
|  | PUMP P-13 | 118 |  |  |  |  |  |  | 450 | VA | DISCONNECT REQUIRED |
|  | UNIT HEATER UH-1 | 117 | 120V, | 10 | 2c#12 | AWG | 1P-15A | B-32 | 160 | VA | DISCONNECT REQUIRED |
|  | CABINET UNIT HEATER CUH-1 | 100 |  |  |  |  |  |  | 160 | VA | DISCONNECT REQUIRED |
|  | GLYCOL PUMP | 118 |  |  |  |  |  |  | 160 | VA | RECEPTACLE REQUIRED |
|  | SPLIT AIR CONDITIONING UNIT AC-1 | 111/ OUTSIDE | 208V, | 10 | 2c#12 | AWG | 2P-15A | A-22/24 | 1800 | VA | DISCONNECT REQUIRED. FEED INDOOR UNIT FROM OUTOOOR UNIT. PROVIDE MIN 3c#12 FOR POWER & CONTROL WIRING. REFER TO MANUFACTIJRER'S LITERATURE PRIOR TO ROUGH-IN. |

_,,---- POLE-MOUNT UTILITY

TRANSFORMER

0--4x 250MCM RWU90 ALUMINUM IN 4" DB2 DUCT. REFER TO SECONDARY TRENCH DETAIL.

L.:::::J

200A, 250V, 7-JAW METERBASE

TO UTILITY STANDARDS

0--4x 250MCM RWU90 ALUMINUM

IN 4" DB2 DUCT.

3P-30A

---0	,;

6

3P-125A

MAIN PANEL 'A'

200A, 120/208V, 30, 42 CCT SERVICE ENTRANCE RATED W/ 200A MAIN BREAKER

◊

l4c#10 AWG RW90 IN EMT/DB2

l4c#1/0  AWG

CONTROL WIRING BETWEEN ATS-1 AND GENERATOR SET AS PER MANUFACTURER'S REQUIREMENT

IN 0B2.

---0	,;

RW90 IN EMT

:-\--- -	-e-  Q- - - - - - -:	!NfEATOR

- I	L4c#1/0 AWG	L.---

~--+---

~--+---

| ELECTRICAL PANEL ' B ' |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CCT. No. | CIRCUIT USE | BREAKER |  | VOLTS |  |  |  | WIRE AND CONDUIT SIZE |  | CCT. So | CIRCUIT USE | BREAKER |  | VOLTS |  |  |  | WIRE AND CONDUIT SIZE |
|  |  | SIZE | POLES |  | " |  | C, |  |  |  |  | SIZE | POLES |  | " |  | C, |  |
|  | GFI RECEPTACLES - ROOMS 106S, 108S, 116 | 15' |  | 120 | 360 |  |  | 2c#12 AWG |  | 2 | LIGHTING - ROOMS 106S-114S | 15' |  | 120 | 320 |  |  | 2c#12 AWG |
| 3 | DATA RECEPTACLES - ROOMS 116, 117 | 15' |  | 120 |  | 480 |  | 2c#12 AWG |  | 4 | LIGHTING - ROOMS 1005-1055 | 15' |  | 120 |  | 430 |  | 2c#12 AWG |
| 5 | RECEPTACLES - ROOM 1095, 111S | 15A |  | 120 |  |  | 480 | 2c#12 AWG |  | 6 | LIGHTING - ROOM 117 | 15A |  | 120 |  |  | 460 | 2c#12 AWG |
| 7 | RECEPTACLES - ROOM 110S, 113S | 15A |  | 120 | 240 |  |  | 2c#12 AWG |  | 8 | 20A GFI RECEPTACLE - ROOM 101S | 2°' |  | 120 | 720 |  |  | 2c#12 AWG |
| 9 | RECEPTACLES - ROOM 102S | 15A |  | 120 |  | 460 |  | 2c#12 AWG |  | 10 | 20A GFI RECEPTACLE - ROOM 101S | 20A |  | 120 |  | 720 |  | 2c#12 AWG |
| 11 | CO DETECTOR - SALLY PORT 117 | 15A |  | 120 |  |  | 500 | 2c#12 AWG |  | 12 | (EF-6XEF-7) EXHAUST FANS | 15' |  | 120 |  |  | 270 | 2c#12 AWG |
| 13 | RECEPTACLES - SALLY PORT 117 | 15A |  | 120 | 480 |  |  | 2c#12 AWG |  | 14 | FRIDGE RECEPTACLE - ROOM 1015 | 15A |  | 120 | 500 |  |  | 2c#12 AWG |
| 15 |  | 15A |  | 120 |  | 540 |  | 2c#12 AWG |  | 16 | FREEZER RECEPTACLE - ROOM 101S | 15A |  | 120 |  | 500 |  | 2c#12 AWG |
| 17 | RECEPTACLES - RMS 103S, 104S. 107S, 1125, 1155 | 15A |  | 120 |  |  | 600 | 2c:#12 AWG |  | 18 | BOILER 8-1 | 15A |  | 120 |  |  | 1440 | AS NOTED |
| 19 | RECEPTACLES - ROOMS 105S | 15A |  | 120 | 540 |  |  | 2c#12 AWG |  | 20 | BOILER B-2 | 15A |  | 120 | 1440 |  |  | AS NOTED |
| 21 | RECEPTACLES - ROOM 116, 117 | 15A |  | 120 |  |  |  | 2c#12 AWG |  | 22 | (]TI BOILER 8-3 | 15' |  | 120 |  | 1440 |  | AS NOTED |
| 23 | <AHU1) AIR HANDLING UNIT AHU-1 | 15A |  | 120 |  |  | 840 | AS NOTED |  | 24 | BOILER 8-4 | 15A |  | 120 |  |  | 1440 | AS NOTED |
| 25 | (AHU2) AIR HANDLING UNIT AHU-2 | 15A |  | 120 | 840 |  |  | AS NOTED |  | 26 | ( FP-1 X FP-2 X FP-3X FP-4) FUEL PUMPS | 15A |  | 120 | 600 |  |  | AS NOTED |
| 27 | (AHU3) AIR HANDLING UNIT AHU-3 | 15' |  | 120 |  | 840 |  | AS NOTED |  | 28 | (HRV1) HEAT RECOVERY VENTILATOR HRV-1 | 15A |  | 120 |  | 480 |  | AS NOTED |
| 29 | <m(ID PUMP P-5, PUMP P-6 | 15A | 2 | 208 |  |  | 850 | AS NOTED |  | 30 | EXHAUST FAN EF-1 | 15A |  | 120 |  |  |  | AS NOTED |
| 31 |  |  |  |  | 850 |  |  |  |  | 32 | (UH-1XCUH1XGF-1) HEATERS, PUMP | 15' |  | 120 | 480 |  |  | AS NOTED |
| 33 | @Xill) PUMP P-7, PUMP P-14 | 15A | 2 | 208 |  | 850 |  | AS NOTED |  | 34 | (HRV2) HEAT RECOVERY VENTILATOR HRV-2 | 15A |  | 120 |  | 250 |  | AS NOTED |
| 35 |  |  |  |  |  |  | 850 |  |  | 36 | (EF-8) EXHAUST FAN EF-8 | 15A |  | 120 |  |  | 200 | AS NOTED |
| 37 | OVERHEAD DOOR MOTOR - SALLY PORT 117 | 20A |  | 120 | 1176 |  |  | 2c#12 AWG |  | 38 | 20A GFI RECEPTACLES - ROOM 1015 | 20A |  | 120 | 720 |  |  | 2c#12 AWG |
| 39 | OVERHEAD DOOR MOTOR - SALLY PORT 117 | 20A |  | 120 |  | 1176 |  | 2c#12 AWG |  | 40 | (EF-9XEF-10) EXHAUST FANS EF-9, EF-10 | 15A |  | 120 |  | 600 |  | AS NOTED |
| 41 |  |  |  |  |  |  |  |  |  | 42 |  |  |  |  |  |  |  |  |
| 43 |  |  |  |  |  |  |  |  |  | 44 |  |  |  |  |  |  |  |  |
| 45 |  |  |  |  |  |  |  |  |  | 46 |  |  |  |  |  |  |  |  |
| 47 |  |  |  |  |  |  |  |  |  | 48 |  |  |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  |  |
| 51 |  |  |  |  |  |  |  |  |  | 52 |  |  |  |  |  |  |  |  |
| 53 |  |  |  |  |  |  |  |  |  | 54 |  |  |  |  |  |  |  |  |
| 55 |  |  |  |  |  |  |  |  |  | 56 |  |  |  |  |  |  |  |  |
| 57 |  |  |  |  |  |  |  |  |  | 58 | FIRE ALARM PANEL | 15A |  | 120 |  | 400 |  | 2c#12 AWG |
| 59 |  |  |  |  |  |  |  |  |  | 60 | EXIT SIGN POWER | 15A |  | 120 |  |  | 200 | 2c#12 AWG |
| VOLTAGE: 120/208VAC MAINS: 200A MAIN BREAKER: N/A BREAKER I.C.. 10KA MOUNTING: SURFACE |  |  |  | PHASE: 3 WIRE: 4 FEEDER: />S INDICATED |  |  |  | FED FROM: AS INDICATED LOCATION: AS SHOWN |  |  |  |  |  |  |  |  |  |  |

~---i---

~-_,

~--+---

L	.,J

TO NON­ ESSENTIAL LOADS

2	30kW/37kVA GENERATOR

| L |  | J | RW90 IN | EMT/DB |
| --- | --- | --- | --- | --- |
| 0- | L AUTOMATIC TRANSFER SWITC (ATS-1). 200A, 250V, 3¢, --4c#I/O AWG RW90 IN EMT |  |  |  |
| 200A, |  |  | 30 SPLITTER |  |

H	120/208V,

4 POLE	3¢,  4W.

NOTE,

ALL CABLES COPPER UNLESS SPECIFICALLY INDICATED OTHERWISE.

SINGLE LINE DIAGRAM

NOT TO SCALE

4,#1/0 AWG

RW90 IN EMT

PANEL 'B'

200A, 30,

120/208V,

60 CCT

4,#1/0 AWG

RW90 IN EMT

PANEL 'C'

200A, 30,

120/208V,

60 CCT

GENERAL ELECTRICAL SPECIFICATIONS

PUMP /

HOUS;:1//

NEW UTILITY POLE

NEW BURIED SERVICE FEEDERS. REFER TO SECONDARY TRENCH DETAIL.

SUPPLY & INSTALL 4"¢ PVC­ DUCT BETWEEN RADIO TOWER AND GENERAL OFFICE 102. BURY MINIMUM 1m BELOW GRADE.

R O A D

- INSTALLATION SHALL BE IN ACCORDANCE WITH THE ONTARIO HYDRO ELECTRICAL SAFETY CODE LATEST EDITION & ALL OTHER APPLICABLE CODES & REGULATIONS.

- ALL EQUIPMENT SHALL BE NEW ANO CSA CERTIFIED.

- ELECTRICAL CONTRACTOR SHALL SUPPLY EQUIPMENT AS SPECIFIED AS WELL AS ANY MISCELLANEOUS TO COMPLETE THE WORK.

- IDENTIFY ELECTRICAL EQUIPMENT WITH PROPER NAMEPLATES. IDENTIFY ALL WIRING, MAINTAIN PHASE SEQUENCE & COLOUR CODING.

- CONTRACTOR TO FURNISH CERTIFICATES OF ACCEPTANCE FROM THE ELECTRICAL INSPECTION DEPARTMENT UPON COMPLETION OF WORK TO THE ENGINEER. VERIFY F/A SYSTEM BY QUALIFIED PERSONNEL. CONDUCT AUDITORY TEST UPON COMPLETION.

- ALL WIRING SHALL BE MIN. #12 AWG Cu. RW90 IN EMT OR AC90 (UNLESS OTHERWISE NOTED). RESIDENTIAL TYPE WIRING (NMD90) WILL NOT BE ACCEPTED.

- INSTALL INSULATED GREEN BONDING CONDUCTOR IN ALL EMT CONDUIT.

- ALL WIRING SHALL BE CONCEALED FROM VIEW UNLESS OTHERWISE NOTED.

- ELECTRICAL CONTRACTOR SHALL MAKE A PERSONAL SITE VISIT AND CONFIRM ALL QUANTITIES/LOCATION/MOUNTING PRIOR TO SUBMITTING QUOTE.

- CONTRACTOR SHALL REPAIR ALL SURFACES DAMAGED DUE TO WORK PERFORMED.

- CONTRACTOR SHALL VERIFY ALL DIMENSIONS, DO NOT SCALE DRAWING.

- ALL MATERIALS REMOVED AND MADE REDUNDANT BY THIS WORK (UNLESS INDICATED OTHERWISE) SHALL BECOME PROPERTY OF OWNER.

15-<I

- MOUNTING HEIGHTS FOR DEVICES AS PER CODE REQUIREMENTS, UNLESS OTHERWISE NOTED.

- MOUNT ALL EMERGENCY LIGHTING AT 7'-6" ABOVE FINISHED FLOOR. WHERE CEILING HEIGHT PREVENTS A 7'-6 MOUNTING HEIGHT, LOWER EMERGENCY LIGHTING AS NECESSARY OR MAKE MINOR ADJUSTMENT OF MOUNTING LOCATION. REQUEST APPROVAL FROM CONSULTANT IF MOUNTING HEIGHT LOWER THAN 7'-0" IS NECESSARY. PROVIDE RECEPTACLE ABOVE CEILING AS REQUIRED.

- COORDINATE ALL LIGHT FIXTURE AND RECEPTACLE INSTALLATION IN MILLWORK WITH CABINET BUILDER.

16. THE INTENT OF THIS PROJECT IS INSTALL A COMPLETE LIGHTING DESIGN. IF SWITCHING FOR AN AREA IS NOT SHOWN, THE ELECTRICAL CONTRACTOR SHALL PROVIDE SWITCHING.

17. ELECTRICAL CONTRACTOR TO SUPPLY AND INSTALL ALL FUSED AND NON-FUSED DISCONNECTS AS REQUIRED FOR ALL MECHANICAL EQUIPMENT INDICATED ON ELECTRICAL AND MECHANICAL DRAWING SETS. AMPERAGE, VOLTAGE AND NUMBER OF POLES TO BE CONFIRMED WITH MANUFACTURER'S LITERATURE.

18. COMPLETE TYPEWRITTEN PANEL SCHEDULES ARE TO BE PROVIDED FOR ALL PANELS.

19. ALL ELECTRICAL EQUIPMENT WITHIN SPRINKLERED ROOMS SHALL BE EQUIPPED WITH HOODS SUITED FOR THE APPLICATION. IF HOODS ARE NOT PROVIDED BY THE FACTORY OR IT IS FOR AN EXISTING PIECE OF EQUIPMENT, IT SHALL BE THE ELECTRICAL CONTRACTORS RESPONSIBILllY TO SUPPLY AND INSTALL THESE HOODS ON NEW OR EXISTING EQUIPMENT AS REQUIRED.

20. ALL CEILING SPACES IN RENOVATION AREAS ACT AS RETURN AIR PLENUMS. ALL CABLING IN CEILING SPACE MUST HAVE AN FT6 FIRE RATING OR BE COMPLETELY ENCLOSEDIN CONDUIT.

W/R EMERGENCY CALL SYSTEM

- PROVIDE LINE VOLTAGE AND LOW VOLTAGE CONNECTIONS FOR ALL COMPONENTS ASSOCIATED WITH THE WASHROOM EMERGENCY CALL SYSTEM INCLUDING, BUT NOT LIMITED TO; OPERATORS, HORNS, PUSHPADS, ELECTRIC STRIKE, L.V TRANSFORMERS, STROBES AND OTHER MISCELLANEOUS COMPONENTS.

- PROVIDE ALL CONDUIT AND WIRING NECESSARY FOR A COMPLITE

WORKING SYSTEM.

- COORDINATE WITH DOOR HARDWARE SUPPLIER/INSTALLER

- PROVIDE POWER FROM BARRIER-FREE DOOR OPERATOR CIRCUIT.

| ELECTRICAL PANEL , C, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CCT. No | CIRCUIT USE | BREAKER |  | VOLTS |  |  |  | WIRE AND CONDUIT SIZE |  | C,C,T. | CIRCUIT USE | BREAKER |  | VOLTS |  |  |  | WIRE AND CONDUIT SIZE |
|  |  | SIZE | POLES |  | " |  | C, |  |  |  |  | SIZE | POLES |  | " |  | C, |  |
|  | COPIER RECEPTACLE - ROOM 102 | 15A |  | 120 | 1000 |  |  | 2c#12 AWG |  | 2 | LIGHTING - ROOMS 100-104 | 15A |  | 120 | 322 |  |  | 2c#12 AWG |
| 3 | DATA RECEPTACLES - ROOMS 103, 104 | 15' |  | 120 |  | 720 |  | 2c#12 AWG |  | 4 | LIGHTING - ROOMS 105-111, 113-115 (EF-2) | 15A |  | 120 |  | 436 |  | 2c#12 AWG |
| 5 | DATA RECEPTACLES - ROOM 102 | 15A |  | 120 |  |  | 720 | 2c#l2 AWG |  | 6 | EXTERIOR LIGHTING | 15A |  | 120 |  |  | 500 | 2c#12 AWG |
| 7 | DATA RECEPTACLES - ROOMS 115, 132 | 15A |  | 120 | 720 |  |  | 2c:#12 AWG |  | 8 | LIGHTING - ROOMS 118, 119, 126 | 15' |  | 120 | 622 |  |  | 2c#12 AWG |
| 9 | DATA RECEPTACLES - ROOM 111 | 15A |  | 120 |  | 360 |  | 2c#12 AWG |  | 10 | LIGHTING - ROOMS 112, 116, 130, 132, 133 | 15A |  | 120 |  | 400 |  | 2c#12 AWG |
| 11 | DATA RECEPTACLES - ROOMS 105, 106, 109 | 15A |  | 120 |  |  | 360 | 2c#12 AWG |  | 12 | LIGHTING - ROOMS 120, 122, 123, 125, 128, 129 | 15A |  | 120 |  |  | 550 | 2c#12 AWG |
| 13 | DATA RECEPTACLES - ROOMS 102, 115 | 15' |  | 120 | 360 |  |  | 2c#12 AWG |  | 14 | EXTERIOR RADIO TOWER LIGHTING | 15A |  | 120 |  |  |  | 2c#12 AWG TECK90 |
| 15 | 20A GFI RECEPTACLES - ROOM 132 | 15A |  | 120 |  | 750 |  | 2c#12 AWG |  | 16 | RECEPTACLES - ROOMS 105, 106 | 15A |  | 120 |  | 480 |  | 2c#12 AWG |
| 17 | MICROWAVE RECEPTACLE - ROOM 132 | 15A |  | 120 |  |  | 1000 | 2c:#12 AWG |  | 18 | BARRIER-FREE DOOR OPERATORS - ROOMS 100, 101 | 15A |  | 120 |  |  | 1000 | 2c#12 AWG |
| 19 | u/c FRIDGE RECEPTACLE - ROOM 132 | 15A |  | 120 | 500 |  |  | 2c#12 AWG |  | 20 | TELEPHONE BOARD RECEPTACLES - ROOM 118 | 15A |  | 120 | 720 |  |  | 2c#12 AWG |
| 21 | FRIDGE RECEPTACLE - ROOM 132 | 15A |  | 120 |  | 500 |  | 2c#12 AWG |  | 22 | (EF-3XEF-4XEF-5) EXHAUST FANS | 15A |  | 120 |  | 640 |  | 2c#12 AWG |
| 23 | GFI RECEPTACLES - ROOMS 101, 108, 111, 113, 133 | 15A |  | 120 |  |  | 720 | 2c#12 AWG |  | 24 | PUMP P-1, PUMP P-2 | 15A |  | 120 |  |  | 500 | AS NOTED |
| 25 | GFI RECEPTACLES - EXTERIOR | 15A |  | 120 | 360 |  |  | 2c#12 AWG |  | 26 | PUMP P-3, PUMP P-4 | 15A |  | 120 | 500 |  |  | AS NOTED |
| 27 | RECEPTACLES - ROOMS 112. 118, 119, 126, 130 | 15A |  | 120 |  | 960 |  | 2c:#12 AWG |  | 28 | <m(ID PUMP P-8, PUMP P-9 | 15A |  | 120 |  | 500 |  | AS NOTED |
| 29 | RECEPTACLES - ROOMS 104, 107, 109, 115 | 15A |  | 120 |  |  | 600 | 2c#12 AWG |  | 30 | PUMPS | 15A | 2 | 208 |  |  | 900 | AS NOTED |
| 31 | RECEPTACLES - RMS 100, 102, 103, 104 | 15A |  | 120 | 720 |  |  | 2c#12 AWG |  | 32 |  |  |  |  | 900 |  |  |  |
| 33 | GFI RECEPTACLES - EXTERIOR | 15A |  | 120 |  | 180 |  | 2c#12 AWG |  | 34 | FUEL MONITORING - ROOM 118 | 15A |  | 120 |  |  |  | 2c#12 AWG |
| 35 | GFI RECEPTACLES - EXTERIOR | 15A |  | 120 |  |  | 180 | 2c#12 AWG |  | 36 | FLUSH VALVE PWR - 121, 124, 127 | 15A |  | 120 |  |  | 500 | 2c#12 AWG |
| 37 | RECEPTACLES - ROOM 111 | 15' |  | 120 | 360 |  |  | 2c:#12 AWG |  | 38 | MECH EQUIPMENT CONTROL CIRCUIT - ROOM 118 | 15A |  | 120 | 500 |  |  | 2c#12 AWG |
| 39 | DATA RECEPTACLES - ROOM 102 | 15A |  | 120 |  | 720 |  | 2c#12 AWG |  | 40 | WATER UNE HEAT TRACE (30mA GFCI-TYPE BREAKER) ROOM 118 | 15' | 2 | 208 |  | 400 |  | 2c#12 AWG |
| 41 | (EF-11) EXHAUST FAN EF-11 | 15A |  | 120 |  |  | 200 | 2c#12 AWG |  | 42 |  |  |  |  |  |  | 400 |  |
| 43 | 20A RACK RECEPTACLE - ROOM 111 | 20A |  | 120 | 720 |  |  | 2c#12 AWG |  | 44 | SANITARY LINE HEAT TRACE (30mA GFCI-TYPE BREAKER) ROOM 118 | 15A | 2 | 208 | 400 |  |  | 2c#12 AWG |
| 45 |  |  |  |  |  |  |  |  |  | 46 |  |  |  |  |  | 400 |  |  |
| 47 |  |  |  |  |  |  |  |  |  | 48 |  |  |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  |  |
| 51 |  |  |  |  |  |  |  |  |  | 52 |  |  |  |  |  |  |  |  |
| 53 |  |  |  |  |  |  |  |  |  | 54 |  |  |  |  |  |  |  |  |
| 55 |  |  |  |  |  |  |  |  |  | 56 |  |  |  |  |  |  |  |  |
| 57 |  |  |  |  |  |  |  |  |  | 58 |  |  |  |  |  |  |  |  |
| 59 |  |  |  |  |  |  |  |  |  | 60 |  |  |  |  |  |  |  |  |
| VOLTAGE: 120/208VAC MAINS: 200A PHASE: 3 FED FROM: />S INDICATED MAIN BREAKER: N/A BREAKER I.C.. 10KA WIRE: 4 LOCATION: AS SHOWN MOUNTING: SURFACE FEEDER: />S INDICATED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

ELECTRICAL SITE PLAN

SECONDARY TRENCH DETAIL

NOT TO SCALE

l=.n

0	16'

32'

j 1/32"=1'-0" 48'

DEC 14 2021

14 St. Paul Street, Suite 201 Thunder Bay, Ontario,P7A 4S5

www.agpeng.com

-	AGEngineering

PROJECT TITLE

DRAWING TITLE

DRAWING SCALE: As Noted

PROJECT No. : A104-21-003

DRAWN BY: GAP

APPROVED BY: MPN

r	Thunder Bay Inc.

Nishnawbe Aski Police Service Electrical Site Plan and

DATE ISSUED: December 2021

DRAWING No.	REV No.

0 ISSUED FOR TENDER

No.

DESCRIPTION

GAP DEC 14 2021

BY

DATE

-

-

New Detachement Building

Single Line Diagram

Electrical Engineers 807•622•3554

Marten Falls First Nation

E1  ffi

HEAT TRACE NOTES

ENSURE MINIMUM 1m CLEARANCE AROUND ,,/ GENERATOR SET. REFER TO ARCHITECTURAL DRAWINGS FDR EXACT LOCATION.

GENERATOR SET

FUEL MONITORING

POWER IDENTIFICATION LEGEND

6

FEED HEAT TRACE CABLE (SUPPLIED AND INSTALLED BY MECHANICAL) FROM 2P-15A GFCI TYPE BREAKER W/ 30mA TRIP. FIELD LOCATE.

C-34

,--7

<ti>	15A DUPLEX RECEPTACLE

$'	4-BUTTON TIMER SWITCH, 1800W RATING, 120V

  - COORDINATE INSTALLATION \IHH MECHANICAL TRADES, MAKE ALL

120V CONNECTIONS AS NEEDED.

  - PROVIDE ADJUSTABLE THERMOSTATIC CONTROL FDR HEAT TRACE

CABLING LOCATED ON EXTERIOR FACE OF BUILDING.

,- - - - _f[ELD_w_c r[ _pJlMPS,__REl:ER _TD_.MECl::_JDWG.5 - - - - - - - - - - - - - - - -- - - - - - - - -UTILITY- - - - - - -

:		P-S		-,-   --,		-	"-r-'	METERBASE THE DESIGNATED CONTROL CIRCUIT SHALL BE USED	:	p.5		p.7		p.11				1'771

BY THE CONTROLS CONTRACTOR AS NEEDED FDR	, c;'-	"+'

THEIR EQUIPMENT. COORDINATE WITH AND PROVIDE	:

---FT-1--­ LP-1

--FT  ----------------------------------------------------------------

LP-2

□

15A TAMPERPROOF DUPLEX RECEPTACLE

15A GFI RECEPTACLE - IN OUTDOOR LOCATIONS MOUNT IN WEATHERPROOF

5/10/15/30 MINUTE PRESET BUTTONS LEVITON# LTB30-1L

ELECTRIC MOTOR

LINE VOLTAGE WIRING AS NEEDED TO FACILITATE	1

r--,	THEIR INSTALLATION. CIRCUIT 'C-38'.	i

:	L---------------------------------------------------------------------------

i

.T'l-.r'I.S	'V''-" C

:J

C0S7

PNL 'A'

BACKBOX W/ SPRING LOADED COVER 20A DUPLEX RECEPTACLE

i	i	20A GFI RECEPTACLE

iZI'

DISCONNECT SWITCH. SIZE AS REQUIRED. OUTDOOR

RATED WHERE REQUIRED.

COMBINATION MAGNETIC MOTOR STARTER C/W H/0/A

s-13 I

I	I ¢0	IB-13

C-27	IL1Ei I

7	8-37 n 8-39	r( F-1)	MECH/

LWATER LINE HEAT LSANITARY LINE HEAT C-20

'0l>

'0l>

C-2D

:l

A

RANGE RECEPTACLE

SELECTOR SWITCH AND AUXILIARY CONTRACTS. SIZED TO MOTOR LOADS.

MAGNETIC CONTACTOR. VOLTAGE AND RATING TO

◊

@t

, \"-,  INTERLOCK EF-1 WITH MOTORIZED

:	:	\	OVERHEAD DOOR MOTORS,	:

I

PROVIDE WIRING TO REMOTE

PANEL

'B'

TRACE, REFER TO NOTES, C-40/ 42.

TRACE, REFER TO

NOTES, C-44/ 46.

TELEPHONE BOARD & GROUND BAR

C-20

AUTO-FLUSH POWER, C-36

BULLPEN	0r

ffiW

AUTO-FLUSH POWER, C-36

fELL#l

SPECIAL CONNECTION FOR POWER SPECIAL RECEPTACLE

DATA & TELEPHONE OUTLET. PROVIDE 3/4"

MATCH CONNECTED MOTOR LOAD. LOW VOLTAGE COIL TO MATCH BUILDING AUTOMATION SYSTEM.

REVERSE-ACTING THERMOSTAT, SUPPLIED BY MECH, INSTALLED BY ELEC.

CO DETECTOR, SUPPLIED BY MECH, INSTALLED BY

1

I

\	DAMPER AND CO DETECTION.	I

\

\	REFER TO MECHANICAL DRAWINGS

I

FOR SEQUENCE OF OPERATION

\ AND COORDINATE AS REQUIRED.

I	OPERATOR, FIELD LOCATE AS

I

N

PER OWNER'S REQUIREMENTS.	I	u'

r-..	I I"

F/A	';'	ATS	II

riu	II

[1m	'

I	ECH \

1 CHASE 3'1

l...!n.J

123

/ MECH

'

1

r '

I c  ASE  I

EMT RACEWAY FROM DEVICE LOCATION TO THE CEILING SPACE IN THE GENERAL OFFICE AREA C/W PULLCORD.

ELEC.

REMOTE FLUSH PUSHBUTTON, SUPPLIED AND

INSTALLED BY MECH, WIRED BY ELEC.

L -\--r- -	-	-	-	-

''

- L 	 J	_J

□

C-27	11

I I

: F P-l===ca	H

'\  124  I'

FP '	FP

TELEPHONE OUTLET. PROVIDE 3/ 4'' EMT RACEWAY FROM DEVICE LOCATION TO THE CEILING SPACE IN THE GENERAL OFFICE

AREA C/W PULLCORD.

CH	'CH' DENOTES DEVICE WALL-MOUNTED AT COUNTER

HEIGHT.

B-13

'' '

'

''

'

'''

SALLY

PORT

DJlJ

4  ]

8-3

Jl

18=)

l...!..!.2J

20A CH

C-lS

4

C-7

J).-r2x 4"¢ EMT CONDUIT

iJ

BETWEEN ROOM 118

II	TELEPHONE & ROOM

II	111 IT RACK

I I

I I

I I

I I

m	]

WASHER/

DRYER

IALL#I 126

c=  J	E	[

IB--,_

# l":S

C-27<tj)

0----

'

'

; '

@-/

C

BARRIER-FREE DOOR OPERATOR. ALL POWER AND CONTROL WIRING BY ELECTRICAL CONTRACTOR. INSTALL CONDUIT AND RECESSED BOXES FDR PUSHBUTTONS AS REQUIRED. COORDINATE WITH DOOR HARDWARE SUPPLIER/INSTALLER.

'

'

''

,'''

CE

8-21

FINGER PRINTING

Q@)

'' '--

GUARDS AREA

DID

MICROWAVE C-17

U/C FRIDGE

BOOKING AREA

I I  [ill]

11

D A-1/3

LAUNDRY/ STORAGE

[I'iQJ

J POWER, C-36

,---------------

'

,

B-13 ,/

,

------

----

-------{§) @cB-1

& BREATH

[JJ]J

8-21  f]

bl

GUARDS

..'!JlB...

C-19	I I

11

MONITOR DEVICESl	I I

SECURE	YOA

o::m

HALL	CELL

01[]

,

□	,,	--

,

c@	,

C-25 bd

/  ,..-,,,..-

B-11	'"

47"AFF►

L.illJ

AT HIGH LEVEL	C-13

I I

'tr	11

C-27

I I

I I

C-27

u

r-,	A

C-31

'  '	'h"

CClV MONITOR	0

ri/	MOTORIZED

l	J	DAMPER

rALL#

1

I I

112	I I

'	'

'

'	'

DEVICES AT

UNIV

CH

1  1 C-5

'

HIGH LEVEL

..'!JlB...

c-u

'  '	COPIER, 36"AF

lJQ1J	7

8-21

B-21

8-21

I I	'	'

REFER TO EMERGENCY

r SATELLITE PHONE CONDUIT

- .... ..._	I

J

'J'

7	8-3

-	'	'

C-1

CALL SYSTEM NOTES.

NEAR ROOF LEVEL PENETRATE

',-_	: MECHANICAL

EM

6

CH "1\

20A 'H'

CH

20A

m	::::J

II

I1 C-5	,  '

□

]

CH	SATELLITE PHONE 3/4"¢ CO DUIT FROM	CONDUIT	I

(EF-4§)  '$[ :)/	,,,

SOFFIT AT HIGHEST ROOF PEAK.

'' , '

"

:<

',	/ MEZZANINE

\	1 7°

,I' I

' · =-	'''''

,-	-B------T7	t3/4"¢ EM;L1- 1

----, ------

-----,- 1- --	EXTERIOR WALL JUST BELOW

1/,

;,;

/'

FREEZER

B-16

FRIDGE 8-8

B-14

B-10

B-38

8-9

8-9

WASHER/ DRYER

A-5/7

(EF-12)Q

LAUNDRY/

C-7

4

C-7

DVR

I	EXTERIOR WALL TERMINATED,IN STANDARD	L	/,C-18 DEVICE BOX AT DESKEIGH!

_..,,---DEVICE BOX FOR 3/4"¢: EMJ BACK TO

8-17

D

I I

II	B-4

;,;

1/' /,

1/,

g

I	ENTRANCE

'

I	1100s I

I

'I

'

MICROWAVE A-8

STAFF ROOM

[j g_j]]

I A:@

RANGE A-2/4

RANGEHOOD

A-6	B-38

CH

FITNESS ROOM 1102s I

8-9

STORAGE

I 103S I

,---;,::	7

I	CDUNG	I

:	ACCESS-=: LI   _--HAfCH-   JI

8-17

HARD

INTERVIEW

DJ:TI	►

C-29

C-29

T

JAN

[JJ]J

ROOM

Dill

REFER TO DETAIL

_,.,..--	SECURITYPANEL. REFE TO:BUILDING ALARM RISER(RADIO E UIP ENT LINK)

o,	:	[2JPACKPOLE

4= --... RADIO TOWER 4"	: C-5 DIA CONDUIT	:

ENTRY POINT	1

C-S THROUGH SLAB.	:

GENERAL OFFICE

[ill]

WAITING AREA

[IQ[]

47"AFF►

1/,

1/,

1/,

1/,

1/,

1/,

1/,

'	D/W1820A@

8-9

DOD	'

71	1/,

##### B'

C-25

8-19

A-8 □0

,---·1.,,...--12•·x4" WIRE MESH CABLING TRAY IN CEILING SPACE TO	:

:  f'

IALL#I	I	I	ACCOMMODATE FUTURE	:

r	109		:  : L  D-AT-A-/V-O-IC-E-C-A-B-LI-N-G.	1j

MEZZANINE ELECTRICAL LAYOUT

B-10

CH

20A

8-9

rALL#j 104S

-Fl

I

L'	J

C-29		C-31

Lr	[	0	ll

0

C-31	'

Lf'7'1,==F=-1"'"a1·-o··

0	2'-0"	4'-0"	6'-0"

L 	,

8-17

D	C-29

  - 4

36"AFFJ

Fl

C-29

q ,....----- CCTV MONITOR

SERGEANT'S OFFICE

[]Q[]	C-31

,,,'

,

,,

'

' ''

WALL MOUNTED LT. RACK PROVIDE /6 AWG GROUND FOR I.T. RACK BACK TO

MAIN BUILDING GROUND IN MECH ROOM 118.

2"¢ CONDUIT FOR STARLINK EXTENDING FROM ROOM 111 UP THROUGH EXTERIOR WALL JUST BELOW HIGHEST ROOF PEAK.

,$$

fl,"AFF

C-16  C-16	EXHIBIT

C-J	DEVICES AT

4	SOFT	'

,, ''

8-19

BATH 1

GUN	ROOM C-16

HIGH LEVEL

INTERVIEW	C-31

[;l-  ,>C-1B

'

'

,,,, '

106S

MUDROOM

0	ON]

VAULT

[J Q[J

CIQiJ

4

C-3	[@]

r'  A

,°"'

20  ' 7

8-19

TRAINING ROOM

I 105S I

' "'

,

'

''

'

''

' / '

''''

'''

'''

'''

B-1

-17

  - 1D	C-16

-If

[

C	1

C-3	C-3

C

J,	,I;	I,	a[

C-3<tj),jf

.,.

20A RACK_}	,

MOUNTED, C-43

'

'

36"AFF	'

'

C-37	'

12"x4n WIRE MESH CABLING TRAY AT CEILING.

/

B-19  ,.,,.,,.,,,

<l:b"-'

' ' '

"

'

"

" "

8-19

'''

'

'

'' '

'

'

' '

8-19

tL10L7S#I

IATH#I 108S

-	7

0	L C

7

r-----------

'

'

'

'

'

'L_ /	1

'

. I	D

-	7

8*-5

*8-7

1

'L--------------------,	'

CABLE TRAY NOTES

0

CABLOFIL WIRE

TELEPHONE BOARD

DVR ROOM

SUPPLY ANO INSTALL ALL NEW CABLE TRAY IN CEILING SPACE. ALL CABLE TRAY SHALL BE WIRE MESH TYPE SIZED AND ROUTED AS INDICATED ON DRAWINGS. EQUAL TO CABLOFIL.

WALL TYPE SUPPORT FDR VERTICAL APPLICATIONS	'

MESH TRAY

C-37

OJI]

r

--........

................

' ' ' '

Rill.Jl.2

' '

'

'

- INSTALLATION OF CABLE TRAY SHALL BE IN ACCORDANCE WITH MANUFACTURER'S RECOMMENDATION.

- ALL CABLE TRAY SHALL BE A GROUNDED IN ACCORDANCE W/ OESC AND MANUFACTURER'S REQUIREMENTS RUN A #6 BARE COPPER GROUND CABLE ALONG ENTIRE CABLE TRAY

LENGTH. BONO TO CABLE TRAY USING APPROVED GROUND LUGS EVERY 50' OF CABLE TRAY LENGTH. TIE CABLE INTO MAIN BUILDING GROUND.

0

MESH TYPE CABLE TRAY.

REFER TO PLAN SHEETS FDR REQUIREMENTS

36"AFF

@=ii>Q,

TIE INTO

LIGHTING

'

'

'''

,'

8-5

8*-5

R_gl_fl

Ulm

8-7

*B-7

8-7

- PROVIDE HANGERS, TRANSITIONS, MOUNTING HARDWARE, GROUND LUGS, CLAMPS AND MISCELLANEOUS EQUIPMENT FOR A COMPLETE INSTALLATION.

- LAY PULL STRING IN CABLE TRAY ALONG ENTIRE CABLE TRAY LENGTH FDR FUTURE CABLE INSTALLATION.

- MOUNT CABLE TRAY MINIMUM 305mm ABOVE LIGHT FIXTURES.

- ALL go· BENDS AND 'T's ARE TO BE RADIUS TYPE. NO SHARP CORNERS ARE PERMITTED.

MESH TYPE CABLE TRAY. REFER TO PLAN SHEETS FOR REQUIREMENTS

CIRCUIT.

□RT

- : OOmm CONDUIT

STUBS IN CEILING SPACES BETWEEN ROOMS 111 & 109.

NOTE,

FOR ALL SWITCHED RECEPTACLES, SWITCH THE UPPER OUTLET ONLY.

POWER LAYOUT

IEST 111S

'r

't

................,....

' '

' ' '

PROJECT No. : A104-21-003

' '' '

8-7

PROVIDE RADIUS 90' AND 'T' KITS TO SUIT LAYOUT.

- INSTALL CABLE TRAY IN AVAILABLE CEILING SPACE. TRANSITION HEIGHTS AS NEEDED AND FULLY COORDINATE WITH ALL OTHER TRADES.

IE1S1T3S

ADJUST CABLE TRAY ROUTING TO AVOID INTERFERENCE WITH MECHANICAL DUCKWORK AND SPRINKLER PIPING.

CABLE TRAY SUSPENSION

NOT TO SCALE

AGEngineering

PROJECT TITLE	DRAWING TITLE

-

CABLE TRAY 90° BEND

NOT TO SCALE

DVR ROOM 111 LAYOUT

1/2"'=1'-0''

0	12"	24'	36"

DRAWING SCALE: As Notsd

DEC 14 2021

B-45

lddF7=1e==F=91"'"01·-o'	r"

0	2'-0"	4'-0'	6'-0"	'

'L	_

DJ.m

B-5

LINEN

8-7

T	T	_

0 ISSUEDFOR TENDER No. DESCRIPTION

GAP DEC 14 2021

BY DATE

Thunder Bay Inc.

r

14 St. Paul Street, Suite201

-	Thunder Bay, Ontario, P?A 4S5

Electrical Engineers t J P	om

Nishnawbe Aski Police Service New Detachement Building Marten Falls First Nation

Power Layout

DATE ISSUED: December 2021 DRAWN BY: GAP

APPROVED BY: MPN

DRAWING No.	REV No.

E2	ffi

LIGHTING IDENTIFICATION LEGEND

,--7

,--------------------------------------------------------------------------------------------------------------------------------------------------------------

A

''

lYPE 'A' - LED CONFINEMENT FIXTURE, SURFACE-MOUNT 50W, 120V, 5000"K, 6250 LUMEN C/W 0-IOV DIMMABLE. CAT#   53-14-A-L2-50-1-4/D-UN-DM

r--7

':c;c- ''

'

'

I

-'-

FIELD LOCATE FIXTURES TO SUIT MECHANICAL EQUIPMENT.

_L

□	□

FOR ALL CELL LIGHT FIXTURES,

  - B	DIMMER CONTROLS MAIN FIXTURE

lYPE 'B' - LED CONFINEMENT FIXTURE, CORNER-MOUNT

B

50W, 120V, 5000"K, 5750 LUMEN, c/w 0-IOV DIMMABLE MAIN FIXTURE, INTEGRAL 3500"K NIGHT LIGHT.

'

:	L---------------------------------------------------------------------------

R

'

'f D

'f D

'f D

'f D

SW3

DMJ

SWITCH CONTROLS NIGHT LIGHT

NEW STAR LIGHTING

CAT# 554-A-L2-50-1-4/D-UN-LN-DB

'	0

'	F=-	A

0	0	0

A	A

MECH/

_L	_L

###### '0	0	'

TYPE 'C' - LED CLOSET LIGHT FIXTURE C/W INTEGRAL OCCUPANCY SENSOR. LEVITON# 9864-LED

I

I	B-6 J I

I

I

L6	J  I

I	I

I	I

1

B-6 J	I

I I

ELEC

[JI[]

D

'fD	'f	'f

0	0	0

B C-12 SW3 OM3

D

BULLPEN

D..m

  - B SW6 DM6

ffiW

L.!n.J

B C-12 SW5 DM5

fELL#l 123

DM4

fELL#j 125

C-12 B SW4 DM4

lYPE 'D' - LED SURFACE WRAP FIXTURE

D		34W, 120V, 4000-K, 4420 LUMEN, 0-10V DIMMING EIKO LIGHTING

0

CAT# LLW-4CP-40K-U

lYPE 'E' - LED TROFFER FIXTURE

23W, 120V, 4000-K, 3250 LUMEN, 0-10V DIMMING HIGH EFFICIENCY, MATTE FINISH, 24"x24"

EIKO LIGHTING

B-6 J

I

#### L

B-6 J

t-6 J

--	--	J

A

B-6 J

SALLY PORT

I

L --	--

A

B-6 J

B-6 J

I

J

..n...	_J

EM5

B-6

-	J

J

]

flt

._, EM4

t:::::J c-8

'

A  ro

0

---------

lJ.l2J

□

A

'

ro

0

---------

MECH

f

crASE

]	121 µ==""

'

ro

IALL#I 126

MECH

crASE t2 124

'

'

ro	ro

0	0 '

-

-

,	,

'

CAT# VOL22-3CP-40K-U

lYPE 'F' - LED WALL-MOUNT FIXTURE, OPAL LENS

A

F	32W, 120V, 4000"K, 4224 LUMEN, 48" LENGTH

EIKO LIGHTING

CAT# STR-3C-40K-U

J

TYPE 'J' - LED LINEAR FIXTURE, 48" LENGTH

30W, 120V, 4000-K, 4000 LUMEN, 0-10V DIMMING CREE CANADA CAT#

EM5 B-6

B-6 J

[JJ1J

B-6 J

B-6 J

r;; s;c ; t,.,.---FI LD LOCATE SWITCHES IN TWO ROWS ALONG

jsw2ifl}YOAcm:	WALL IN GUARD AR A, PROVIDE LAB LS.

1DM2:Efr

LS4C-40L-40K-10V-FD/AC5-18/5-48-QI 4B-JB/ ACS-48-QI 4B-TB

KQ	lYPE 'K' - LED 6" DOWNLIGHT FIXTURE

A

'  3D	A	C

ISDWM3t:lEt}fBr ULLPEN	A

12W, 120V, 4000"K, 1030 LUMEN, 0-10V DIMMING

A

1

Q	C-10

2	EM/13

,  D4

BOOKING

CDM1I 2

YOA

MEDIUM BEAM, SEMI-SPECULAR FINISH, CLEAR REFLECTOR

C-6

0	A	0 '

--,

'-Efr

1sw .fA'}cm 111

I DM4::t:A,

'  D

ISW5ifl}cm /2	0

AREA

om

0

CELL

0

0.1[]

CREE LIGHTING ESSENTIA SERIES HOUSING CAT# S-DL-6-1IL-40K

B-6 J

B-6 J

B-6 J

''''

10M5-EA,

P bl

SW6'i:A}cm f3	u

0	DM2

TRIM CAT# S-DL6T-SS-C

,-----------------

ORANGE BX WIRE

□

C-6

--------------

FINGER PR NTNG & BREATH

[JJ]J

A

C-10

''

'

'I'

I

jI /	0

GUARDS

.J!J.B

LillJ

IALL#I

0

112  C-10

D

DM6iY7

--

I

GUARDS AREA

DID

EM3

..n...

EMI

SECURE HALL

CJ.1[J

C-2

SW2 C-12 B

cc

C-2

Q

C-6

TYPE 'p' - LED SURFACE-MOUNT CANOPY FIXTURE 66W, 120V, 4000'K, 7500 LUMEN, WHITE FINISH CREE LIGHTING IG SERIES

[]

CAT# IG-NM-5S-J-40K-UL-WH/IG-JB

oD	lYPE 'Q' - LED ADJUSTABLE WALLPACK FIXTURE

26W, 120V, 4000"K, 2954 LUMEN, PHOTOCELL

[]

GREEN EMT CONDUITS

7

ENTRANCE 1100s I

g

I

'

'

BLUE EMERGENCY LIGHTS

I I

A	flt

0

GENERAL OFFICE [IQ[]

[iJ

## r

'

'

EMy	PS

0

C-2

,,

,.. ,., ,., I

UNIV

I	"

[iJ

N4j8l

RAB DESIGN LIGHTING

CAT# AWL-LED26W-A-4K-BRZ-PCA

lYPE 'N4' - LED SURFACE-MOUNT FIXTURE

20W, 120V, 4000-K, 2000 LUMEN, WHITE FINISH,

10.4" DIA, LED 0-IOV DIMMING

IMPACT RESISTANT, WHITE OPAL POLYCARBONATE LENS

FC LIGHTING# FCW3050-120V-LED4K- 2000-WH-LD

lYPE 'N5' - LED SURFACE-MOUNT FIXTURE 38W, 120V, 4DOO"K, 3600 LUMEN. WHITE FINISH,

14" DIA, LED 0-IOV DIMMING

IMPACT RESISTANT, WHITE OPAL POLYCARBONATE LENS

------

I

'

FC LIGHTING# FCW3060-120V-LED4K-3600-WH-LD

'I	[iJ

WAITING	''

UI	lYPE 'UI' - LED UNDERCABINET FIXTURE, 12" LONG

'

##### B'

C-6

YELLOW UNDERGROUND CONDUITS

[]

L	,

C-6

Q

TRAINING ROOM

I105S I

I

'

'''

'

D

7EM7

MUDROOM

0

om

C-4

[iJ

'

'"

I

I'

M	GUN

VAULT

[@]

D	D

,	y,-FI

EXHIBIT ROOM

0'	Dfil

''

'

','□'--□

I'

-2

0	-	'

om

SERG ANT'S OFFICE

,r-

[iJ

C-2

C-2

Ml

c-2g

;rMI

C-2

SOFT

AREA

0

[IQ[]

'' C-2

0

C-2

C-6

CZ,

$

$'w

I OW, 120V, 400D'K, 380 LUMEN C/W CONNECTORS, TERMINATIONS KITS AND MISCELLANEOUS FOR A COMPLETE INSTALLATION. COORDINATE EXACT MOUNTING LOCATIONS WITH ARCHITECTURAL DRAWINGS/ELEVATIONS.

SSL eCOVELINE# ECVL-1-4K-120

TOGGLE SWITCH

THREE-WAY TOGGLE SWITCH

SLIDE DIMMER SWITCH, lYPE TO MATCH FIXTURE AND/OR DRIVER lYPE.

PIR WALL SWITCH OCCUPANCY SENSOR LIGHTING CONTROL RATED 800W @ 120V

LEVITON# ODSIS-1D

COMBINATION DIMMER SWITCH AND PIR OCCUPANCY SENSOR, 0- IOV DIMMING

N4 '

B2- 1	F

'	0	0

[iJ

OM]

INTERVIEW	[]

LUTRON# NS-Z101

INFRARED OCCUPANCY SENSOR, LINE VOLTAGE, 450 SOFT

EM7	''	LI

[

COVERAGE, CEILING MOUNTED.

8-2

1' :0

B-2

C	o□c-s	1

o□c-s

LEVITON # ODC04-IDW, OR EQUAL

'

'

I I

B-2 1'

N4!8)

-	7

L_O

REFLECTED CEILING LEGEND

'NL'

'NL' DENOTES AN UNSWITCHED NIGHT LIGHT FIXTURE.

NEW EMERGENCY 12 voe LIGHTING UNIT C/W INTEGRAL 12VDC 6W LED MR16 HEAD(S) AS INDICATED.

SIZED FOR 0.5HR COVERAGE.

EMERGI-LITE# JMLC SERIES

-	7

N5l<>< 8-2 l('.:x

,.,............ ----D 1-

IALL#j ' ' 107S

I'

I

B-2	/ ''

N4!8r'

[iJ

0

0

0

SUSPENDED ACOUSTIC CEILING TILES @ g' -0" AFF

TILE TO BE CGC - OLYMPIA - FINE TEXTURED PANEL

SECURllY CEILING SYSTEM C/W SUSPENSION SYSTEM.

2- 5/8" DRYWALL- PAINTED

5/8" TYPE 'x' DRYWALL CEILING AT g'-o" PAINTED

5/8" PLYWOOD

SECURITY WIRE MESH-AMICO

1/2" lYPE 'X' DRYWALL PAINTED ON 3 5/8"- 16 GA. METAL FURRING @ 16" O.C.

0

SLOPED 1/2'' DRYWALL PAINTED CEILING ON RESILIENT

CHANNELS

0

SLOPED 5/8" lYPE 'X' DRYWALL PAINTED CEILING ON

RESILIENT CHANNELS

REMOVABLE ARMSTRONG METALWORKS SECURELOCK CEILING

SYSTEM C/W SUSPENSION SYSTEM.

EMERGENCY LIGHTING 12 voe 6W LED MR16 DOUBLE REMOTE HEAD(S). WIRED TO PACK EM# (USE #ID AWG AC90 MIN. FOR

1 ZVDC WIRING). WALL/CEILING MOUNT AS INDICATED ON DRAWINGS. EMERGI-LITE# JMLC SERIES

LED "RUNNING MAN" EXIT SIGN W/ PICTOGRAM SYMBOLS CONFORMING TO ISO 7010. EXTRUDED ALUMINUM FRAME

W/ CLEAR POLYCARBONATE PANELS AND PICTOGRAM FILMS.

SELF-POWERED WITH NICKLE-CADMIUM BATTERY SIZED FOR

2 HOURS BACKUP. UNIVERSAL VOLTAGE

oD

C-6

"

IE1S0T9S'1'

0	''

'

'

'

'

: <§	' '

I'

IEST #/

I IOS

DoC-6

5/8" lYPE 'X' DRYWALL

0	1/2" DRYWALL PAINTED CEILING ON 2,6 CEILING JOISTS

SECURE ACCESS PANEL LOCATED IN CEILING

(120V-347V). SINGLE OR DOUBLE FACED

TO SUIT AND PICTOGRAM FILMS TO DENOTE EXIT DIRECTIONS AS NOTED ON DRAWINGS. EMERGI-LITE# EA SERIES

LIGHTING LAYOUT

IE1S1T1S'1

I

B-2 1

N4!8)

lJ..im

LINEN

DJ.m

IE1S1T3S'I

EXTERIOR LIGHTING NOTE

ALL EXTERIOR LIGHT FIXTURES SHALL BE CONTROLLED BY REMOTE PHOTOCELL. ELECTRICAL CONTRACTOR TO PROVIDE PHOTOCELLS, LIGHTING CONTACTORS AND ALL OTHER NECESSARY EQUIPMENT

r	-

FOR A COMPLETE WORKING SYSTEM.

AGEngineering

Thunder Bay Inc.

PROJECT TITLE	DRAWING TITLE

Nishnawbe Aski Police Service Lighting Layout

DRAWING SCALE: As Noted

DATE ISSUED: December 2021

DEC 14 2021

PROJECT No. : A104-21-003

DRAWING No.	REV No.

l  d F7= =www..::IF=,1.,4••a1'-D"

0	2'-0"	4'-0"	6'-0"

T 	 _ 	 T 	_

Q

C-6

0 ISSUED FOR TENDER

No. DESCRIPTION

GAP DEC 14 2021 BY DATE

-

Electrical Engineers

14 St. Paul Street, Suite 201 Thunder Bay, Ontario,P7A 4S5 807 622 3554

•	•

www.agpeng.com

New Detachement Building Marten Falls First Nation

DRAWN BY: GAP APPROVED BY: MPN

E3	ffi

,--7

,--------------------------------------------------------------------------------------------------------------------------------------------------------------

1	EC14	EC13

,:	IZJ::,	cC8J

SYSTEMS IDENTIFICATION LEGEND

.;:]	FIRE ALARM PULLSTATION, 2-STAGE

FIRE ALARM HORN/STROBE

W: q- r	_.

r--1	 ------------------------------------- 	J	I:

- - - - - - - - - - - - -

_.:_	- -T-	-  -  -  -  -  -  -  -	--,	-fl EC12	□	□

IZJ::,

HEAT DETECTOR

FIXED TEMPERATURE HEAT DETECTOR

''	I

### '  ---------------n---------------

I

'	I	I	I	I	:

I	I	I	I	:

IF/A ZONE a j

MECH/

2x 100mm INCOMING TELEPHONE SERVICE CONOUITS ENTRY POINT.  0

0

VP

©	@)

IF/A ZONE 1 j

r---------,----------1	,

I

i	i

I

I I I

VP

I	@) ©

IONIZATION SMOKE DETECTOR

LINE VOLTAGE COMBINATION SMOKE ALARMS C/W VISUAL STROBE, BATTERY BACKUP, TEMPORAL SOUND PATTERN AND SILENCE BUTTON. BATTERY SIZED TO PROVIDE 7 DAYS BACKUP POWER. TIE INTO 120V LIGHTING CIRCUIT AHEAD OF SWITCHING. INTERCONNECT ALL SMOKE ALARMS SO THAT THE ACTUATION OF ONE COMBINATION SMOKE ALARM WILL CAUSE ALL SMOKE ALARMS TO SOUND. CEILING-MOUNT

I	I	I	I

I	I	I	I

1,	ELEC

[JJ [J

:

F/A

BULLPEN

D..m

VP	'VP' DENOTES DEVICE WITH PENITENTIARY GRADE

VANDAL-PROOF COVER

I	I	I	I	I	v%l1

EE	SECURITY KEYPAD

L		J	L		J	 --- --- - ------ 	"'o-_:-

icJ	I	IC4

DOOR CONTACT

,-----------------

□

SALLY PORT

[JJ]J

IF/A ZONE 91

[ill

:[I

r	1	'

FINGER PRINTING & BREATH

[JJ [J

GUARDS

-'!!LB_

l  illJ

l...!..!.2J

bl

LillJ

GUARDS

AREA

DID

PHONE

[J]1J

©VP

[I

A

IF/AZONE10j

JAN

[]JI]

BOOKING

om

AREA

IC4

CJ:,

[I I

I

/,	I

[,-------.!I'- o

I I

c>a'v I

]

LAUNDRY/ STORAGE

[IiQJ

IALL#I

126

E

EMERGENCY CALL SYSTEM NOTES ON DWG 'E1'

r

REFER TO W /R

IC7

cD

MOTION SENSOR (CEILING MOUNT)

CARD ACCESS LOCATION

[I	ELECTRIC STRIKE

@)	CELL CEILING MICROPHONE

DURESS PANIC BUTTON

8	B	DURESS ALARM SOUNDER

;

[ill	LOW TEMPERATURE SENSOR

0-

MIRCOPHONE ON/OFF TOGGLE SWITCH

"

\_ EXTERIOR FIRE ALARM STROBE DEVICE TO ACTIVATE UPON FIRST STAGE ALARM.

ffil

WALL MIRCOPHONE

g

I I

'I

'I

'

'	FITNESS

B	ROOM

I

I	1102s I

'

'

ciL

..,

I

I

HARO

INTERVIEW

[JJ3J

I

,-.- - - - - - -.	_ I.!J

I

JAN

[JJ]J

rALL#] 109

DVR ROOM

Dill

[I

O:J

I F/A ZONE 2 j

GENERAL

OFFICE

[ill]

FIELD LOCATE PUSHBUTTONS\ IN GENERAL OFFICE FOR

FIRE ALARM ANNUNCIATOR

[I

PANEL

WAITING AREA [J]QJ

EXTERIOR CAMERA LOCATION

INTERIOR CAMERA LOCATION

\;('	INTERVIEW ROOM CAMERA LOCATION

IZ)J	CORNER-MOUNT CELL CAMERA LOCATION CC#

'I	rALL#j

[JI

.;:]

[l [EE-"I

REMOTE RELEASE OF DOOR D-4 AND 0-5.

_	,

1

,

BUILDING SECURITY SYSTEMS/IT WORK

:<i//J

IF/AZONE 1 I

104S	I	J	1	0

U-

1

THE INSTALLATION OF SECURITY, CARD ACCESS, CCTV, DURESS AND IT SYSTEMS SHALL BE

1	COMPLETED BY BAY LOCK AND SECURITY. A CASH ALLOWANCE HAS BEEN IDENTIFIED IN THE

[}]	□

L 	,

B	LT

D

liiijj

lpjill	lpjill

'ZY	Fl	I(.'.'..>'

EE	©

EXHIBIT

SERGEANT'S

OFFICE

CCTV	[IQ[]

I

I "

:

lnol	SOFT	,	.;:j [I	I

SPECIFICATIONS TO COVER THE SECURITY CONTACTOR'S WORK. THE CONTRACTOR SHALL CARRY BAY LOCK AS A SUB-CONTRACTOR, COORDINATE THE INSTALLATION AS NEEDED AND PROVIDE ANY LINE VOLTAGE POWER CONNECTIONS THAT MAY BE REQUIRED. THE ELECTRICAL CONTRACTOR MUST PROVIDE EMPTY CONDUIT SYSTEMS, RACEWAYS, JUNCTION BOXES, DEVICE BOXES AND OTHER COMPONENTS AS MAY BE NECESSARY TO SUPPORT BAY LOCK AND

SECURITY'S INSTALLATION. BAY LOCK AND SECURITY'S WORK WILL CONSIST OF, BUT MAY NOT

BATH 1 106S

MUDROOM

[JQ[]

©	ROOM

GUN	..,	[@J

uOuN]

MONITORS

,E§J	INTERVIEW	"" 	]l	_J

[IQij	@)	L',lJ ;- ,' - -	,_11"- - - -

I	u

BE LIMITED TO, THE FOLLOWING:

- BUILDING AND DURESS ALARM SYSTEMS

  - SUPPLY AND INSTALLATION OF ALL LOW VOLTAGE WIRING

0-..

[I	0,0

0-..

0/)v>

I	TELEPHONE OUTLET

{B	I	INTERCOM HANDSET,

  - SUPPLY AND INSTALLATION OF DURESS PUSHBUTTONS, TEMPERATURE SENSORS AND ALARM SYSTEM HARDWARE.

<	/	t,i'-) I

FIELD LOCATE.

c. SYSTEM PROGRAMMING, COMMISSIONING AND DEMONSTRATION.

TRAINING

ROOM

11ass I

I I I I

I	II- - - - - - - - -

©

1

rALL# 107S

IATH#I

108S

. I

### LI	---- -;-------------- --L_1j  - d,==f,t ------------

I	EC7	EC8

I	7

I	L a

I

I

D	I

I

I

- INTERVIEW ROOM CCTV/MIC SYSTEM

a. SUPPLY AND INSTALLATION OF ALL LOW VOLTAGE WIRING

b. SUPPLY AND INSTALLATION OF CAMERAS, MICS, RECORDING DEVICES AND SYSTEM HARDWARE

c. SYSTEM PROGRAMMING, COMMISSIONING AND DEMONSTRATION

.3. BUILDING AND CELL CCTV/MIC SYSTEM

- SUPPLY AND INSTALLATION OF ALL LOW VOLTAGE WIRING

- SUPPLY AND INSTALLATION OF CAMERAS, MICS, RECORDING DEVICES, EQUIPMENT RACK AND SYSTEM HARDWARE.

L--------------------7   I I I

IEST #11 109S

I

I

IEST 11 1IOS

I

SECURITY/CAMERA SYSTEM NOTES

c. SYSTEM PROGRAMMING, COMMISSIONING AND DEMONSTRATION

  - CARD ACCESS SYSTEM

    - SUPPLY AND INSTALLATION OF ALL LOW VOLTAGE WIRING

I I I I I

" I

I

I	Rfil1_3

Ll.!.liJ

- !.J.ru

IEST #I

11JS

  - ELECTRICAL CONTRACTOR SHALL SUPPLY AND INSTALL ALL CONDUITS, JUNCTION BOXES, PULL BOXES AND OEVICE BOXES FOR THE NOTEO EQUIPMENT AND LOCATIONS.

  - ELECTRICAL CONTRACTOR SHALL COORDINATE WORK WITH SECURITY CONTRACTOR FOR EXACT MOUNTING DETAILS.

  - ELECTRICAL CONTRACTOR SHALL SUPPLY AND INSTALL A 3/16" PULLCORD IN ALL CONDUITS FOR INSTALLATION OF CABLES BY THE SECURITY CONTRACTOR.

- ELECTRICAL CONTRACTOR SHALL SUPPLY AND INSTALL CONDUIT BETWEEN THE 40" MONITOR IN THE GENERAL OFFICE 102 TO THE DVR ROOM 111.

- PROVIDE 2X 1OOMM CONDUIT BETWEEN TELEPHONE BOARD IN ROOM 118 AND TELEPHONE BOARD IN ROOM 111.

- ALL CELL CAMERA CONDUITS SHALL BE STUBBED INTO CELL.

- ELECTRICAL CONTRACTOR SHALL SUPPLY AND INSTALL THE FOLLOWING DEVICE BOXES:

  - INTERIOR & EXTERIOR CAMERAS (EXCLUDING CELL CAMERAS) - SINGLE-GANG BOX

  - CELL CORNER-MOUNT CAMERAS - CONDUIT STUB ONLY. NO BOX.

  - KEYPADS - SINGLE GANG BOX

  - DURESS BUTTONS - SINGLE GANG BOX

  - MICROPHONE TOGGLE SWITCH - SINGLE GANG BOX

  - CEILING MICROPHONES - CONDUIT STUB ONLY. NO BOX.

  - WALL MICROPHONE - SINGLE GANG BOX.

- ALL CONDUIT SHALL BE EMT ANO ALL INTERIOR SURFACE BOXES SHALL BE CAST ALUMINUM. ALL JUNCTION BOXES SHALL BE STAMPED STEEL. NEMA 12. ALL CONDUITS SHALL BE EQUIPPED WITH PLASTIC BUSHINGS WITHIN BOXES AND ENCLOSURES.

    - SUPPLY AND INSTALLATION OF CARD READERS, STRIKES, POWER SUPPLIES AND SYSTEM HARDWARE.

c. SYSTEM PROGRAMMING, COMMISSIONING AND DEMONSTRATION

  - IT WIRING

a. SUPPLY AND INSTALLATION OF CAT6 TELEPHONE AND DATA CABLING INCLUDING TERMINATIONS, COVER PLATES, LABELING AND CAT6 VERIFICATION.

b. SUPPLY AND INSTALLATION OF IT RACK INCLUDING CAT6 PATCH PANELS AND HORIZONTAL/VERTICAL CABLE MANAGERS.

c. INSTALLATION AND TERMINATION OF VOICE AND FIBRE RISER CABLES BETWEEN DVR ROOM AND MECHANICAL/SPRINKLER ROOM INCLUDING APPROPRIATE PATCH PANELS AND/OR BIX TERMINATIONS.

I

I

SYSTEMS LAYOUT	1I

o	2'-0"	4'-0'	6'-0"

lddF7= ==F="li ,,,..a,. o-	cs	L

LINEN

T	T	_

DJ.m	JI

AGEngineering

-

r	14 St. Paul Street, Suite 201

Thunder Bay Inc.

-

0

ISSUEDFOR TENDER

GAP

DEC 14 2021

-

PROJECT TITLE	DRAWING TITLE

Thunder Bay, Ontario, P?A 4S5 807 622 3554

Nishnawbe Aski Police Service Systems Layout New Detachement Building

DRAWING SCALE: As Noted

DATE ISSUED: December 2021

DRAWN BY: GAP

DEC 14 2021

PROJECT No. : A104-21-003

DRAWING No.	REV No.

E4	ffi

'L	_

IZJ::,

EC6

No. DESCRIPTION

BY DATE

Electrical Engineers

www• .agp•eng.com

Marten Falls First Nation

APPROVED BY: MPN

|  | 3/4"¢ |  |
| --- | --- | --- |
| 6Hx6" JUNCTION BOX |  | 6I EMT |
|  | 3/4"; IEMT 6 |  |

| GUARD SECURE ------------------------------7 FIRE ALARM PANEL NOTES, AREA HALL #1 ZONE 1 - STAFF ROOM / REST ROOMS i 1. REFER TO PLANS FOR QUANTITIES AND LOCATIONS OF 132 119 2-STAGE ------------------------------ DETECTION AND SIGNALING DEVICES. '1 Wr ADDRESSABLE ZONE 2 - OFFICE AREA i 2. ALL FIRE ALARM DEVICES SHALL BE ADDRESSABLE. DEDICATED - FIRE ALARM ------------------------------ 3. ALL DETECTION DEVICES SHALL BE WIRED AS CLASS 'A'. CIRCUIT PANEL ZONE 3 - MECHANICAL/ELECTRICAL ROOM i 1/2"¢ Ul L1/2"¢ ------------------------------1 4. ALL SIGNALING DEVICES SHALL BE WIRED AS CLASS 'A'. EMT EMT ZONE 4 - CELL #1 i 5. THE AUTOMATIC SPRINKLER SYSTEM SHALL BE EQUIPPED ------------------------------ WITH TAMPER, WATERFLOW AND PRESSURE DETECTING REMOTE ZONE 5 - CELL #2 I DEVICES FOR EACH SPRINKLER ZONE AND SHALL BE SECURE SALLY SALLY 1 ANNUNCIATOR ------------------------------: MONITORED BY THE FIRE ALARM CONTROL PANEL. HALL #2 PORT PORT ZONE 6 - CELL #3 i COORDINATE W/ MECHANICAL AND SPRINKLER DRAWINGS. 112 117 117 FIRE DEPT­ ------------------------------1 MAKE CONNECTIONS TO ALL DITECTION DEVICES. ' !EID B [EID CONNECTION ZONE 7 - BULL PEN i 6. FIRE ALARM ZONE REQUIREMENTS MAY CHANGE AS A D3 D4 DS I 3/4"¢ ------------------------------ RESULT OF SPRINKLER SYSTEM DESIGN. ELECTRICAL t 3/4"¢ t 1/2"¢ 1/2"¢ EMT ZONE 8 - YOA CELL i 6 IRCl ------------------------------: CONTRACTOR TO COORDINATE W/ SPRINKLER INSTALLER. EMT EMT EMT PTZ ZONE 9 - SALLY PORT I 7. PROVIDE SIGNAL BOOSTERS AND ISOLATION MODULES AS ------------------------------1I REQUIRED TO MEET APPLICABLE CODES AND FOR A HARD INTERVIEW ZONE 10 - INMATE AREA i COMPLETE WORKING SYSTEM. SECURE SECURE I 3/4"¢ r\ ROOM 115 ------------------------------ 8. PROVIDE GENERATOR "RUN" AND GENERATOR "TROUBLE" HALL #3 HALL #3 1/2"0 EMT I.T. 6"x6" 6 EMT LJ IRC2 PROVIDE 3x NORMALLY CLOSED SIGNALS TO FIRE ALARM SYSTEM FROM NEW GENERATOR ALARM 126 126 CELL# 1 122 ROOM JUNCTION RELAY -- DRY CONTACTS FOR TIE-IN TO SET. EACH CONDITION SHALL REGISTER A SEPARATE CABINET 111 BOX BUILDING SECURITY SYSTEM. TROUBLE SIGNAL ON THE FIRE ALARM SYSTEM. SURFACE ? ? 0HC CELL#2 123 r3/4"¢ 3/4"¢ 1/2"¢ L1/2"¢ EMT L1/2"¢ 1"¢ EMT EMT EMT EMT MECHANICAL/ TO GUARD AREA 6 --4----0c CELL#3 125 ATf---,'>------,Mf---<0 {(C EMT ROUTE CONDUIT FIRE ALARM RISER SPRINKLER SECURE HARD 132 DESK, ROOM 118 HALL #2 INTERVIEW FIELD LOCATE. NOT TO SCALE 112 115 BULLPEN 120 ' ? t !EID 3/4"¢ 09 Y.O. CELL 129 6I EMT IRC3 L11r• 1/2"¢ PTZ [] ELECTRIC EMT EMT GENERAL SOFT STRIKE WAITING AREA 100 OFFICE INTERVIEW 3/4"0 SOFT INTERVIEW 3/4"¢ 3/4"¢ EMT ENTRANCE DOOR 10t2 103 3/4\;i EMT I.T. 6"x6" 6I EMT Lr\J ROOM 103 [ EMT CARD ALARM EC2 ROOM JUNCTION IRC4 ACCESS CABINET !EDID10 D!E7ID1 111 BOX JUNCTION BOX 3/4"¢ EMT !Cl t1/2"¢ 1/2"¢ 6 CJ, 3/4"¢ 3/4"¢ 1/2"¢ ELECTRIC EMT ORV ROOM EMT EMT ' [] STRIKE 111 [ EMT EMT EMT WAITING AREA 100 TO ATf---,'>------,Mf---<0 {(C 3/4"0 3/4"¢ EMT 3/4"¢ EMT- IC3 [ EMT CARD GENERAL OFFICE 102 D ACCESS NOTE: 3/4"¢ EMT I PRIOR TO ROUGH-IN. MAKE ADJUSTMENTS AS NECESSARY 6 JUNC D r\ JUNCTION BOX CONFIRM CONDUIT ROUTING WITH SECURITY CONTRACTOR 61-1/4"0 EMT IC4 3/4"0 TO FACILITATE SECURITY DEVICES/COMPONENT INSTALLATION. BOX 6I EMT LJ [] ELECTRIC IC2 IC9 STRIKE GENERAL OFFICE 102 3/4"¢ 3/4"¢ EMT TO HALLWAY #2112 3/4"¢ EMT FINGERPRINT & [ EMT CARD DURESS ALARM RISER ACCESS I.T. r\ BREATH ROOM 116 JUNCTION BOX NOT TO SCALE 3/4"¢ EMT ROOM LJ IClO 111 CC! [] ELECTRIC 1"¢ EMT CC2 1/2"0 STRIKE DVR ROOM 111 DOOR 6 JUNC ,; · 3/4"¢ 3/4"¢ EMT BOX CC3 [ffi---B @ [ EMT CARD ACCESS r=-------r------1 CC4 JUNCTION BOX I EXTERIOR 1/2"¢ I 3/4"¢ EMT NOTE, [] ELECTRIC I EMT I 1"¢ EMT JUNC ccs CONFIRM CONDUIT ROUTING WITH SECURITY CONTRACTOR STRIKE ENTRANCE 100S 6 BOX PRIOR TO ROUGH-IN. MAKE ADJUSTMENTS AS NECESSARY 3/4"¢ 3/4"0 EMT 13/4"¢ FUERANK FUERANK : CC6 TO FACILITATE SECURITY DEVICES/COMPONENT INSTALLATION. [ EMT CARD ENTRANCE DOOR EMT FT-1 FT-1 I ACCESS FUEL MONITORING I JUNCTION BOX (LOW FUEL) I 3/4"¢ EMT INTERVIEW & BREATH ROOMS CCTV/MIC RISERS L_ J 1"¢ EMT r ELECTRIC 6 ,J:;;U;::NC::7--e-tPICS NOT TO SCALE [] STRIKE SALLY PORT 117 ,:--------------7 BOX ENTRANCE DOOR I STAFF ROOM 101S 1/2"¢ c ,y ;.,IC6 3/4"¢ 3/4"¢ EMT l I I EMT I r MECH/ 10"x10" [ EMT CARD SPRINKLER JUNCTION ACCESS :9 El36 [fl: ROOM 118 BOX JUNCTION BOX I L 3/4"0 KEYPAD LOW TEMP I 3/4"¢ EMT L EMT ALARM J ROOM JUNCTION 6 CJ, JCS DVR 12"x12" l [] ELECTRIC 111 BOX , 7 STRIKE HALLWAY #1119 3/4"0 3/4"0 EMT TO SALLY PORT 117 ,:--------------7 3/4"¢ EMT I EXHIBIT ROOM r7 I [ EMT CARD MECHANICAL/ DVR 1 GENERAL OFFICE 102 .. l ,.----,:,-J:8;}:, EC1 I 105 LJ I ROOM I I 112 0 I ACCESS SPRINKLER 111 EMT 1 EMT I IC11 I JUNCTION BOX ROOM 11r8 I 9 El3 6 [fl I "¢ ,J:;;U;::NC'."f-e-[2JJ EC12 J I L I 6 I I ELECTRIC ALARM ALARM I 3/4"¢ KEYPAD LOW TEMP I LB:'.:O'.'..X,..f-'?-[2JJEC13 [] STRIKE CABINET 1 "¢ EMT CABINET L EMT ALARM J II 3/4"0 1/2"¢ 1/2''• II EXHIBIT ROOM 105 DOOR Y'>-j:8;J::,EC14 I EMT EMT I EMT I 3/4"¢ 3/4"¢ EMT (SURFACE (SURFACE r-------, 9 Qfil PIR 6 iQg I [ EMT CARD 10"x14" 1o"x14" 3/4"¢ EMT ORV ROOM 111 ACCESS JUNCTION JUNCTION !ROOM 116 ---- --7 1"¢ EMT L3/4"¢ JUNCTION CEILING KEYPAD DOOR I JUNCTION BOX BOX) BOX) I I 6 ,J-U-NC7-A-l"x'hEC3 I EMT BOX MOUNT CONTACT I I r;,1 I LB:'.:O'.'..X_!-0- JJEC4 1O"x10" I MOTION I ELECTRIC l t.lc!J CCTV L SENSOR [] STRIKE II 3/4"¢ LOW TEMP II UNDER GUN VAULT 106 DOOR CABINET 3/4"0 3/4"¢ EMT L EMT ALARM _J 3/4"¢ EMT [ EMT CARD ACCESS 611"¢ EMT JUNC ECS , 7 JUNCTION BOX !SALLY-PORT 117- - - - 7 BOX EC6 I GUN VAULT r7 I I I EMT I 106 LJ I 0---3/4"¢ [] ELECTRIC I l r;,1 I r I IC12 I STRIKE HALLWAY #5109 I t.lc!J I I I [ EMT TO HALLWAY #3104S EMT ALARM 61"0 EMT 1 EC7 I 3/4"¢ 1/2"¢ 1/2"0 I 3/4"¢ 3/4"¢ EMT I 3/4"¢ LOW TEMP I 3/4"¢ EMT 1 "0 CARD L _J ALARM EMT ALARM II I ACCESS CABINET CABINET EMT EMT I EMT I JUNCTION BOX ECB 9 JBf-E>----{IPIR)-B---tt, 6 iQg I rI G:EN:ER-A-L O-F-FIC-E -1-02--7 EC9 L3/4"¢ JUNCTION CEILING KEYPAD DOOR I [] ELECTRIC MECHANICAL/ L _J I EMT BOX MOUNT CONTACT 1 STRIKE MUDROOM 107 : ,,,,+RADIO EQUIPMENT LINK, 3/4"¢ EMT SPRINKLER I MOTION I 3/4"¢ 3/4"¢ EMT ENTRANCE DOOR I l_ / "¢ LJ' I STANDARD 2, 4" BOX 1"¢ EMT IJ:;;U:::Nc::7-&--C2JJ EC10 ROOM 118 L SENSOR [ EMT CARD 3 4 6 JUNCTION BOX ACCESS IL EMT I LB:'.:O'.'._X_!-0-[8JJ EC11 _J NOTE: NOTE: NOTE: NOTE: CONFIRM CONDUIT ROUTING WITH SECURITY CONTRACTOR CONFIRM CONDUIT ROUTING WITH SECURITY CONTRACTOR CONFIRM CONDUIT ROUTING WITH SECURITY CONTRACTOR CONFIRM CONDUIT ROUTING WITH SECURITY CONTRACTOR PRIOR TO ROUGH-IN. MAKE ADJUSTMENTS AS NECESSARY PRIOR TO ROUGH-IN. MAKE ADJUSTMENTS AS NECESSARY PRIOR TO ROUGH-IN. MAKE ADJUSTMENTS AS NECESSARY PRIOR TO ROUGH-IN. MAKE ADJUSTMENTS AS NECESSARY TO FACILITATE SECURITY DEVICES/COMPONENT INSTALLATION. TO FACILITATE SECURITY DEVICES/COMPONENT INSTALLATION. TO FACILITATE SECURITY DEVICES/COMPONENT INSTALLATION. TO FACILITATE SECURITY DEVICES/COMPONENT INSTALLATION. CARD ACCESS SYSTEM RISER BUILDING ALARMS RISER CAMERA/MIC SYSTEM RISER EXHIBIT & GUN VAULT CCTV I ALARM RISER DEC 14 2021 NOT TO SCALE NOT TO SCALE NOT TO SCALE NOT TO SCALE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0 | ISSUED FOR TENDER | GAP | DEC 14 2021 | r - AGEngineering Thunder Bay Inc. 14 St. Paul Street, Suite 201 Thunder Bay, Ontario, P7A 4S5 Electrical Engineers 807.622.3654 www.agpeng.com | PROJECT TITLE Nishnawbe Aski Police Service New Detachement Building Marten Falls First Nation | DRAWING TITLE Systems Riser Diagrams | DRAWING SCALE: As Noted | PROJECT No. : A104-21-003 |  |
|  |  |  |  |  |  |  |  | DATE ISSUED: December 2021 | DRAWING No. E5 | REV No. ffi |
|  |  |  |  |  |  |  |  | DRAWN BY: GAP |  |  |
|  |  |  |  |  |  |  |  | APPROVED BY: MPN |  |  |
|  | No. | DESCRIPTION | BY | DATE |  |  |  |  |  |  |